## 10.05.23
THERMAX CHEMICAL DIVISION COOLING WATER TREATMENT REPORT
Daily Service Report For Cooling Water Treatment MFL - Power Plant
Date:10.05.2023
Sr No. | Parameter | UOM | Make-Up Water |  | Circulating water
|  |  | Design Limit | Actual Value | Design Limit | CT-1&2 | CT-3 | CT-4
[6 empty] | Actual Value | Actual Value | Actual Value
| Make up Water | M3/Day |  |  |  | 2911 | 1785 | 1150
| Blowdown | M3/Day |  |  | 780 | - | - | -
| Delta T | Deg C |  |  | 9 | 7.4 | 5.6 | 3
1 | pH |  | 7.8-8.2 | 8.62 | 8.5 to 9.0 | 8.54 | 8.5 | 8.48
2 | Conductivity | µs/cm | <300 | 206 | <4200 | 2170 | 1856 | 2510
3 | TDS | ppm | 150 | 133.9 | <2750 | 1410.5 | 1206.4 | 1631.5
4 | Sample Temp | Deg C |  |  |  | 45.2 | 40 | 35
5 | P Alkalinity | ppm as CaCO3 | NIL | 20 | ppm | 20 | 20 | 20
6 | M Alkalinity | ppm as CaCO3 | 150-240 | 140 | <400 | 200 | 170 | 170
7 | Chloride | ppm as CaCO3 | 21 | 42 | <450 | 440 | 355 | 455
8 | Total Hardness | ppm as CaCO3 | 5 | 2 | <200 | 70 | 54 | 74
9 | Ca- Hardness | ppm as CaCO3 | 3 | 1 | <100 | 44 | 34 | 48
10 | Mg- Hardness | ppm as CaCO3 | 3 | 0.4 | <60 | 16 | 12 | 20
11 | O-PO4 | ppm as PO4 |  | - | 5.0-7.0 | 7 | 6.8 | 6.6
12 | SiO2 | ppm as SiO2 | 15 | - | <150 | - | - | -
13 | Zinc | ppm as Zn |  | - | 0.5-1.5 | - | - | -
14 | Iron | ppm as Fe | 0.2 | - | <3 | - | - | -
15 | Sulphate | ppm as SO4 |  | - | <1200 | - | - | -
16 | COC |  |  | - | 11.0 to 12.0 | 10.534 | 9.0097 | 12.1845
17 | LSI |  |  | - | 1 TO 2 | 0.84 | 0.56 | 0.7
18 | RSI |  |  | - | 5.5 TO 7.0 | 6.72 | 7.24 | 7.02
19 | FRC | - |  | - | 3 to 5 | 0.1 | 0.1 | 0.1
20 | Turbidity | NTU | 1 | 1 | <20 | 5 | 5.9 | 8.2
| Date | TBC / ml |  |  | SRB/ml
|  | <10000 |  |  | <10/100 ml
CT-1&2 | 14.04.2023 | 100000 |  |  | 10
CT-3 | 14.04.2023 | 100000 |  |  | 10
CT-4 | 14.04.2023 | 100000 |  |  | 10
Chemical |  | CT-1 &2 |  | CT -3 |  | CT -4
|  | Proposed | Actual | Proposed | Actual | Proposed | Actual
|  | Kgs/ Day | Kgs/Day | Kgs/ Day | Kgs/Day | Kgs/ Day | Kgs/ Day
Maxtreat 7702 | Daily | 4.01 | 4.01 | 2.06 | 2.06 | 2.2 | 2.2
Maxtreat 370 | Daily | 0.8 | 0.8 | 0.4 | 0.4 | 0.44 | 0.44
Maxtreat 7202 TR | Daily | 2 | 2 | 1 | 1 | 1.1 | 1.1
Maxtreat CL -5 | Daily | 1.2 | 1.2 | 0.6 | 0.6 | 0.66 | 0.66
Maxquat 7960 | Once a Week | 8.1 | 0 | 12 | 0 | 12 | 0
Maxtreat 606 | Once a alternate Month | 81 | 0 | 120 | 0 | 120 | 0
Maxtreat 652 | Once a alternate Month | 81 | 0 | 120 | 0 | 120 | 0
Maxtreat 7960 (Chlorine activator Once a Week) |  | Added on--> | 05.05.2023 | Added on--> | 05.05.2023 | Added on--> | 05.05.2023 | DOSING SHALL BE DONE ON THE BASIS OF TBC AND SRB RESULTS
|  | Due on --> | 12.05.2023 | Due on --> | 12.05.2023 | Due on --> | 12.05.2023
Max-606 (NOB once a alternate Month) |  | Added on--> | 18.04.2023 | Added on--> | 27.04.2023 | Added on--> | 18.04.2023
|  | Due on --> |  | Due on ----> |  | Due on ---->
Max-652 (NOB once a alternate Month) |  | Added on--> | 14.03.2023 | Added on--> | 14.03.2023 | Added on--> | 14.03.2023
|  | Due on --> |  | Due on ----> |  | Due on ---->
CHEMICAL STOCK DETAILS
Chemical Name | Frequency | Opening Stock | Praposed Qty. | Actual Consumption Kg |  | Closing Stock kg.
Maxtreat 7702 | Daily | 197.6 | 8.27 | 8.27 |  | 189.33
Maxtreat 370 | Daily | 54.2 | 1.64 | 1.64 |  | 52.56
Maxtreat 7202 TR | Daily | 30 | 4.1 | 4.1 |  | 25.9
Maxtreat CL -5 | Daily | 16 | 2.46 | 2.46 |  | 13.54
Maxquat 7960 | Once a Week | 61.6 | 32.1 | 0 |  | 61.6
Maxtreat 606 | Once a alternate Month | 599 | 321 | 0 |  | 599
Maxtreat 652 | Once a alternate Month | 280 | 321 | 0 |  | 280
Remarks:
1) Please Avoid excess Blowdown in CT-1&2 and CT-3 Because COC is Lower than Design Limit.
2) Next SRB/TBC due on 14/05/23.
3) COC calculation base on Conductivity.
| 121 | 700 |  |  | 30
| 75 | 701 |  |  | 28.8 |  |  | 3130 | 110 | 205.2 | 10 | 20 | 67 | 0.52 | 0.13 | 970 | 75 | 705 | 27.5 | 32.5 | 9.1 | 1056 | 90 | 430 | 85.2 | 2 | 4 | 60 | 0.54 | 0.13 | 320 | 78 | 704 | 27 | 33 | 7.84 | 6180 | 0 | 130 | 395.2 | 15 | 31 | 3.68 | 89 | 0.53 | 0.14 | 1300 | SHUT | DOWN | SHUT | DOWN | 29 | 7 | * | 18 | 2.3 | 2.5