## Chiller-Process
THERMAX LIMITED CHEMICAL DIVISION COOLING WATER TREATMENT REPORT
Daily Service Report For Chiller MFL - Process Plant
Date: 10.05.2023
Sr No. | Parameter | UOM | DESIGN LIMIT | CA-1 Chiller | CA-2 Chiller | CMS Chiller
|  |  |  | Actual Value | Actual Value | Actual Value
1 | pH |  | 8.5-9.5 | 8.62 | 8.65 | 8.64
2 | Conductivity | us/cm | <1600 | 852 | 490 | 1250
3 | TDS | ppm | <1040 | 553.8 | 318.5 | 812.5
4 | Iron | ppm | <20 | 0.6 | 0.5 | 0.5
5 | Nitrite | ppm | >1000 | 75 | 750 | 700
5 | consumption | KG |  | 0 | 0 | 0
Remarks:
| 121 | 700
| 75 | 701 |  |  |  |  | 110 | 205.2 | 10 | 20 | 67 | 0.52 | 0.13 | 970 | 75 | 705 | 27.5 | 32.5 | 9.1 | 1056 | 90 | 430 | 85.2 | 2 | 4 | 60 | 0.54 | 0.13 | 320 | 78 | 704 | 27 | 33 | 7.84 | 6180 | 0 | 130 | 395.2 | 15 | 31 | 3.68 | 89 | 0.53 | 0.14 | 1300 | SHUT | DOWN | SHUT | DOWN | 29 | 7 | * | 18 | 2.3 | 2.5

## Cooling Tower
THERMAX LIMITED CHEMICAL DIVISION COOLING WATER TREATMENT REPORT
Daily Service Report For Cooling Water Treatment MFL - Process Plant
Date:10.05.2023
Sr No. | Parameter | UOM | Make Up Water Analysis |  | ALL CT | NaOH-CCU | CA-1 | KOH | H202 | CA-2 | CMS- PRO | CMS-VAM | ECH | CPVC
|  |  | Design Limit | Actual Value | Control Limit | Actual Value | Actual Value | Actual Value | Actual Value | Actual Value | Actual Value | Actual Value | Actual Value | Actual Value
Limit
| Make up Water | M3/Day |  |  |  | 228 | 180 | 457 | 298 | 898 | - |  | 44 | -
| Blowdown | M3/Day |  |  |  | - | - | 15 | - | - | - | - | - | -
1 | pH |  | 8.0-8.2 | 8.63 | 7.2 to 7.8 | 7.7 | 7.48 | 7.75 | 7.71 | 7.76 | 7.83 | 7.75 | 7.5 | -
2 | Conductivity | µm/cm | <300 | 206 | 3400 | 2210 | 1732 | 1778 | 1806 | 1032 | 1401 | 1617 | 1872 | -
3 | TDS | ppm | <150 | 133.9 | <2200 | 1436.5 | 1125.8 | 1155.7 | 1173.9 | 670.8 | 910.65 | 1051.05 | 1216.8 | -
4 | Sample temp. | Deg C |  |  |  | 36.2 | 30.1 | 30.5 | 32.4 | 30.2 | 30.6 | 32.4 | 33.5 | -
5 | COC |  |  | - | 9 | 10.7282 | 8.4078 | 8.6311 | 8.767 | 5.0097 | 6.801 | 7.8495 | 9.0874 | -
6 | P Alkalinity | ppm | 0 | 20 | NIL | NIL | NIL | NIL | NIL | NIL | NIL | NIL | NIL | -
7 | M Alkalinity | ppm | 150-240 | 140 | <100 | 70 | 50 | 70 | 70 | 80 | 80 | 80 | 50 | -
8 | Chloride | ppm | <21 | 42 | <300 | 362 | 212 | 326 | 320 | 183 | 305 | 347 | 369 | -
9 | Total Hardness | ppm | <240 | 150 | < 1200 | 1208 | 766 | 1142 | 890 | 572 | 788 | 890 | 1188 | -
10 | Ca- Hardness | ppm | <144 | 100 | < 600 | 840 | 530 | 794 | 618 | 396 | 544 | 620 | 826 | S/D
11 | Mg- Hardness | ppm | <100 | 40 | < 400 | 358 | 226 | 338 | 262 | 166 | 230 | 264 | 350 | -
12 | O-PO4 | ppm |  | - | 3.0-5.0 | 5.1 | 3.5 | 5.2 | 3.3 | 3.1 | 3.5 | 3.3 | 5 | -
13 | SIO2 | ppm | <15 | - | <100 | - | - | - | - | - | - | - | - | -
14 | FE | ppm | <0.2 | - | <3 | - | - | - | - | - | - | - | - | -
15 | Zinc | ppm |  | - | 0.5-1.5 | - | - | - | - | - | - | - | - | -
16 | LSI |  |  | - | 1 - 2 | 0.36 | 0.18 | 0.5 | 0.4 | 0.34 | 0.61 | 0.55 | 0.12 | -
17 | RSI |  |  | - | 5.5 - 7.0 | 6.51 | 7.01 | 6.5 | 6.67 | 6.92 | 6.48 | 6.52 | 7.06 | -
18 | FRC | ppm |  | - | <2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | -
19 | Turbidity | NTU | <1 | 1 | <20 | 5 | 5.8 | 8.8 | 8 | 6 | 5.9 | 5.1 | 5.8 | -
ALL CT | DATE | TBC / ml |  |  |  |  | SRB/ml
|  | <10000 |  |  |  |  | <10/100 ml
NaOH-CCU | 2023-04-28 | 10000 |  |  |  |  | 10
CA-1 | 2023-04-28 | 1000 |  |  |  |  | 10
KOH | 2023-04-28 | 10000 |  |  |  |  | 10
H202 | 2023-04-28 | 10000 |  |  |  |  | 10
CA-2 | 2023-04-28 | 1000 |  |  |  |  | 10
CMS- Utility | 2023-04-28 | 10000 |  |  |  |  | 10
CMS Process | 2023-04-28 | 10000 |  |  |  |  | 10
ECH | 2023-04-28 | 10000 |  |  |  |  | 10
CPVC | 2023-04-28 | 10000 |  |  |  |  | 10
Chemical |  | NaOH-CCU |  | CA-1 |  | KOH |  |  | CA-2
|  | Proposed | Actual | Proposed | Actual | Proposed | Actual |  | Proposed | Actual
|  | Kgs/ Day | Kgs/Day | Kgs/ Day | Kgs/Day | Kgs/ Day | Kgs/Day |  | Kgs/ Day | Kgs/Day
Maxtreat 7702 | Daily | 0.8 | 0.8 | 1.0667 | 1.07 | 1.1378 | 1.14 |  | 2.1333 | 2.13
Maxtreat 370 | Daily | 0.16 | 0.16 | 0.21333 | 0.21 | 0.22756 | 0.23 |  | 0.42667 | 0.43
Maxtreat 7202 TR | Daily | 0.4 | 0.4 | 0.53333 | 0.53 | 0.56889 | 0.57 |  | 1.0667 | 1.07
Maxtreat CL -5 | Daily | 0.24 | 0.24 | 0.32 | 0.32 | 0.34133 | 0.34 |  | 0.64 | 0.64
Maxquat 7960 | Once a Week | 2.1 | 0 | 3.15 | 0 | 4.05 | 0 |  | 6.9 | 0
Maxtreat 606 | Once a alternate Month | 21 | 0 | 31.5 | 0 | 40.5 | 0 |  | 69 | 0
Maxtreat 652 | Once a alternate Month | 21 | 0 | 31.5 | 0 | 40.5 | 0 |  | 69 | 0
Maxtreat 7960 (Chlorine activator Once a Week) |  | Added on--> | 2023-05-05 | Added on--> | 2023-05-05 | Added on--> | 2023-05-05 |  | Added on--> | 2023-05-05
|  | Due on --> | 2023-05-12 | Due on --> | 2023-05-12 | Due on --> | 2023-05-12 |  | Due on --> | 2023-05-12
Max-606 (NOB once a alternate Month) |  | Added on--> | 2023-04-18 | Added on--> |  | Added on--> | 2023-04-18 |  | Added on-->
|  | Due on --> |  | Due on --> |  | Due on --> |  |  | Due on -->
Max-652 (NOB once a alternate Month) |  | Added on--> | 14.3.2023 | Added on--> | 14.3.2023 | Added on--> | 13.10.2022 |  | Added on--> | 2022-11-14
|  | Due on --> |  | Due on --> |  | Due on --> |  |  | Due on -->
Chemical | Frequency | H202 |  | CMS |  | ECH |  |  | CPVC
|  | Proposed | Actual | Proposed | Actual | Proposed | Actual |  | Proposed | Actual
|  | Kgs/ Day | Kgs/Day | Kgs/ Day | Kgs/Day | Kgs/ Day | Kgs/Day |  | Kgs/ Day | Kgs/Day
Maxtreat 7702 | Daily | 0.71111 | 0.71 | 1.28 | 1.28 | 1.5644 | 1.56 |  | 0.39111 | 0
Maxtreat 370 | Daily | 0.14222 | 0.14 | 0.256 | 0.256 | 0.31289 | 0.31 |  | 0.078222 | 0
Maxtreat 7202 TR | Daily | 0.35556 | 0.36 | 0.64 | 0.64 | 0.78222 | 0.78 |  | 0.19556 | 0
Maxtreat CL -5 | Daily | 0.21333 | 0.21 | 0.384 | 0.384 | 0.46933 | 0.47 |  | 0.11733 | 0
Maxquat 7960 | Once a Week | 2.7 | 0 | 2.4 | 0 | 4.5 | 0 |  | 0.75 | 0
Maxtreat 606 | Once a alternate Month | 27 | 0 | 24 | 0 | 45 | 0 |  | 7.5 | 0
Maxtreat 652 | Once a alternate Month | 27 | 0 | 24 | 0 | 45 | 0 |  | 7.5 | 0
Maxtreat 7960 (Chlorine activator Once a Week) |  | Added on--> | 2023-05-05 | Added on--> | 2023-05-05 | Added on--> | 2023-05-05 |  | Added on--> | 2023-05-05
|  | Due on --> | 2023-05-12 | Due on --> | 2023-05-12 | Due on --> | 2023-05-12 |  | Due on --> | 2023-05-12
Max-606 (NOB once a alternate Month) |  | Added on--> | 2023-04-08 | Added on--> |  | Added on--> | 2023-04-01 |  | Added on-->
|  | Due on --> |  | Due on --> |  | Due on --> |  |  | Due on -->
Max-652 (NOB once a alternate Month) |  | Added on--> | 14.11.2022 | Added on--> | 14.3.2023 | Added on--> | 14.3.2023 |  | Added on--> | 2023-01-15
|  | Due on --> |  | Due on --> |  | Due on --> |  |  | Due on -->
CHEMICAL STOCK DETAILS
Chemical Name | FREQUENCY | Stock as on 10.05.2023 | Chemical Received | OPENING STOCK | Cons. Kg/Day | Closing Stock kg. | Proposed / Day |  | Chemical Remains Days
Maxtreat 7702 | Daily | 88.03 | 0 | 88.03 | 8.69 | 79.34 | 9.08 |  | 8.7379
Maxtreat 370 | Daily | 22.18 | 0 | 22.18 | 1.736 | 20.444 | 1.82 |  | 11.233
Maxtreat 7202 TR | Daily | 60.8 | 0 | 60.8 | 4.35 | 56.45 | 4.55 |  | 12.4066
Maxtreat CL -5 | Daily | 116.5 | 0 | 116.5 | 2.604 | 113.896 | 2.72 |  | 41.8735
Maxquat 7960 | Once a Week | 54.9 | 0 | 54.9 | 0 | 54.9 | 26.55 |  | 2.0678
Maxtreat 606 | Once a alternate Month | 342.5 | 0 | 342.5 | 0 | 342.5 | 265.5 |  | 1.29
Maxtreat 652 | Once a alternate Month | 651 | 0 | 651 | 0 | 651 | 266 |  | 2.4474
Remarks :
1) Please keep Blowdown close in CA-2, CMS VAM and CMS PRO Because COC is Lower than Design Limit.
2) Please give Blowdown in CCU Because COC is Higher than Design Limit.
3) CPVC cooling tower is in Shutdown condition.
4) ECH cooling tower one cell is in closed condition.
5) Next SRB/TBC due on 14/05/23.
6) CLO2 dosing system is stopped Because M-7961 chemical is finished.
| 121 | 700 |  |  | 30 | 38.8 | [9 empty] | 20
| 75 | 701 |  |  | 28.8 | 34.2 | [8 empty] | 10 |  | 67 | 0.52 | 0.13 | 970 | 75 | 705 | 27.5 | 32.5 | 9.1 | 1056 | 90 | 430 | 85.2 | 2 | 4 | 60 | 0.54 | 0.13 | 320 | 78 | 704 | 27 | 33 | 7.84 | 6180 | 0 | 130 | 395.2 | 15 | 31 | 3.68 | 89 | 0.53 | 0.14 | 1300 | SHUT | DOWN | SHUT | DOWN | 29 | 7 | * | 18 | 2.3 | 2.5
Note on J85: Nimesh Shah: Weakly dose. Per dose qty.
Note on J86: Nimesh Shah: Per dose qty.
Note on J87: Nimesh Shah: Per dose qty.